## Slide 1: Energy transition - Project
Zazie Heinesch - Guayaquil

## Slide 2: Outline
Technologies used
Electrical mix, first idea
Improvement idea
Weather and topography analysis
Mathematical model for a dam
Final electrical mix
Conclusion

## Slide 3: Technologies
Photovoltaic panels
Wind turbine
Battery
Import
Export
But also :
Implementing in a model of expansion planning

## Slide 4: Model formulation
Market clearing:
Import :
Export :
Technologies :
Power :
Energy not served :
Fuel cost :

## Slide 5
Storage equation :

## Slide 6
CO2 emissions :
CO2 maximum:
Curtailment:
Total cost (objective function):

## Slide 7: PV panels
Source: Danish Energy Agency (Technology Data for Generation of Electricity and District Heating)
unlimited capacity
Efficiency of 20.5%
Lifetime of 35 years
Investment cost = 870 k€/MW
O&M fixed = 10.6 k€/MW/y
O&M variable = 10 €/MWh/y

## Slide 8: Wind turbine
 unlimited capacity
Efficiency of 47%
Lifetime of 27 years
Investment cost = 1.11 M€/MW
O&M fixed = 16.4 k€/MW/y
O&M variable = 2 €/MWh/y
Source: Danish Energy Agency (Technology Data for Generation of Electricity and District Heating)

## Slide 9: Battery
Battery of 3 MW
 Maximal capacity of 12 MWh
Efficiency of 85 %
State of charge
State of charge ∈[0.2;0.8]
Investment cost = 500 k€/MWh
During 4h
Lifetime = 25 years
Battery of 3 MW
 Maximal capacity of 12 MWh
Efficiency of 85 %
Investment cost = 500 k€/MWh
During 4h
Lifetime = 25 years
Source : Invinity data sheet (https://invinity.com/wp-content/uploads/2024/12/Invinity-ENDURIUM-Data-Sheet-MAR000020-2024-12.pdf?_gl=1*lzgj6v*_up*MQ..*_gs*MQ..&gclid=CjwKCAiA65m7BhAwEiwAAgu4JFqYz_U4PtidA2i2jJlRaFiS13FNLzbv9fz0VtaHFF2xsj7x1VRSZBoCTVQQAvD_BwE)

## Slide 10: National grid
Import and Export
Export price of 20 €/MWh
Composed of 80 % of hydropower
 import not expensive
 Unlimited capacity
Import price of 74 €/MWh

## Slide 11: Demand
Electrical consumption of 31.6 GWh
Colling produce with absorption chiller  solar pannel and biomass, so no electrical consumption.
 total demand of 31.6 GWh

## Slide 12: Electrical mix – First version
7.1 MW of wind turbine
12.9 MW of PV
1.562 M€
LCOE = 49.40 €/MWh

## Slide 13: Comparaison with results of last semester
P
This semester
LCOE = 49 €/MWh
Wind turbine = 7.1 MW
PV = 12.9 MW
Energy stored = 0 GWh
Last semester
LCOE = 60 €/MWh
Wind turbine = 4.9 MW
PV = 4.4 MW
Energy stored = 3.5 GWh
Same import and export price, but enhance of renewable energy and battery prices which were not accurate (particullary information about PV).

## Slide 14: A step further
The national energy mix contains 80% hydropower. However, hydropower prices vary significantly depending on rainfall.
 Design and implementation of a dam on campus, along with analysis over several weather years using uncertainty model.

## Slide 15: Topography analysis
Head of 150m
River available on the campus
Installation of the dam there

## Slide 16: Weather analysis
Source: Renewable ninja (https://www.renewables.ninja)
Dry year
Humid year
Average year

## Slide 17: Precipitation translation
CF =
=
[MWh]
Dimensionalised using an average year (2022) as reference.

## Slide 18: Precipitation translation
Constant converting all the precipitation in power
 is the variable representing the installed power of the power plant. The value of is adimensionalised with . It will be multiplied later by , a variable representing the installed capacity.
[h]

## Slide 19: Assumptions
Uncertainty is applied on the model
Propability of 60% of an average year, based on precipitation.
Probablility of 20% for a dry year
Probability of 20% for a humid year.

## Slide 20: Dam
Capacity stored : 100 MWh
Empty in 20h
Assume already constructed
 Investment price of 0 €/MWh
Efficiency of 75%
Lifetime = 75 years

## Slide 21: Dam storage equations
Balance :
Initial state :
Where T is the last time step
No environmental flow is considered
Only power generation, no pumping.

## Slide 22
Capacity max :
Discharge max :
Energy stored range:
This maximum capacity corresponds to a reservoir holding 326 200 m³ of water.
There is no minimum water required in the reservoir

## Slide 23: Final electrical mix
Power installed
PV panels : 17.4 MW
Wind turbine : 32 MW
Dam : 5 MW (20h)
Battery : 3 MW (4h)

## Slide 24
Dry year
Humid year
Total cost : 3.4 M€  LCOE = 106.60 €/MWh

## Slide 25: Why doesn’t the dam store more ?
There is a strong seasonal contrast between the humid and dry periods in Ecuador.
There was more water in 2017 due to extrem rainfall.
When extrem rainfall occurs, the reservoir is quicly full, so the excess water is splilled rather than stored. In 2017, 80 % of water was spilled from the dam.

## Slide 26
2022
2017

## Slide 27: Conclusion
Integrating the dam on the campus allows to observe the variability of hydropower in Ecuador.
These fluctiations cause variations in the cost of importing electricity from the national grid.
The final Levelized cost of Electricity (LCOE) is much higher, since more renewable energy sources must be available to meet electricity demand, even when water suffly is insufficient.
Link to the online repositery : https://github.com/Zazhein/Energy_transition

## Slide 28
Thank you!